## Sheet1
Functionality Response Document (Exhibit 3)
Instructions: Proposers shall respond to all items noted below which make up the Scope of Services for RFP 19-56. As requested in the table below, please confirm how the proposed Facilities Maintenance Services being offered meets the specific service requirement as a "standard," "optional," or is "not available." In addition, the Proposer shall provide a description of how the service requirement is delivered and disclose any special requirements (of any kind) that would be necessary in order to deliver the noted service requirement. A response is required for each line; additional information may be included in supplemental form and shall be clearly indexed and documented for ease of reference. If service requirement is not included as part of the solution, please describe what alternative you are proposing.
| Service Delivered |  | Description of how service is delivered | Special Requirements
| Standard (included in price) | Not Available
3. Scope of Services - General Requirements
3.1. The Contractor shall provide 24-hour comprehensive operations and maintenance service to all locations with daily hours of operations as described, but not limited to, herein.
3.2. Provide at least (1) one full-time Residence Manager (RM) or General Manager (GM) who shall administer the program on a full time basis in consultation with the Director of Facilities Engineering/Maintenance (FE/M).
3.3. The contractor will also provide one (1) full-time Computer Maintenance Management System (CMMS) manager who will provide software and support to the program. The RM or GM will serve on the Facilities Engineering/Maintenance operations team. The RM or GM shall be on duty during the regular schedule that is delineated by HCC. Additional work hours may be required of the RM or GM as requested by the Director of FE/M or designee. The RM or GM is a contract employee through this contract and may be requested to supervise other contract employees while working in conjunction with HCC Facilities Administration. The RM/GM and the CMMS Representative will commit 100% of their time to this project/contract.
3.4. Provide account management to ensure services are delivered consistent with the stated scope of services, specifications and service expectations. Management services shall include sourcing, supervising and evaluating current service delivery methods and submitting enhancement opportunities to improve quality, customer service, and cost performance as well as satisfying current and new operational business requirements.
3.5. Provider shall follow all code regulations, safety regulation recommendations shall be followed within relation to any and all work accomplished under this contract.
3.6. Provide management services for all issues related to equipment and associated components of equipment included within the scope of the RFP.
3.7. Provider shall be the subject matter expert and consultant for the college to ensure services are delivered per required codes and industry standard practices, consistent with agreement term of work completed by third-party vendor or performed by maintenance contractor.
3.8. Provider shall monitor any sub-contractor/third party contractor performance.
3.9. Develop, maintain a library of facilities drawings, operation and maintenance manual, safety programs, and emergency procedures per HCC, federal, state and city guidelines.
3.10. Provide the expertise supervision, maintenance repair and project management services associated with building systems within designated facilities. Ensure all systems function and operate per design, maintain operational reliability and conserve energy usage.
3.11. Provide and identify improvement opportunities to increase reliability of operation, extend life cycle of equipment and reduce operation cost to include the conservation of energy usage.
3.12. Provide dedicated account management, administrative, certified technical staff consistent with the industry standard personnel qualifications. Staffing plans are to satisfy daily maintenance and service workload and coverage objectives consistent with established service level agreements, service level response goals, and other HCC requirements.
3.13. Staffing considerations include:
3.13.1. Develop staffing plans that minimize overtime expenses by planning and scheduling, in advance, recurring work tasks assigned to staff that are on off-shifts and/or split shifts.
3.13.2. Develop operating plans and strategies which ensure that adequate resources are available at all times to properly support or respond to the scale and technical complexity of the building systems equipment, events, and/or occurrences.
3.14. Provide monthly, quarterly and year-to-date operational reporting services which highlight operational issues/conditions and summarize the preventive maintenance, remedial work requests and facility management operations. Reports to be prepared at the Facility level with applicable portfolio summaries presented. (Portfolio – All facilities included within this document; Facilities added during the course of agreement)
3.15. Operate CMMS platform to effectively integrate the work order processing and reporting functions. Contractor shall effectively manage the work order processes for remedial service requests and preventive maintenance work, etc.
3.16. Monitor technical subcontracted vendors ensuring services are delivered consistent with agreement terms and service specifications. As necessary, update service specifications based on changing business needs with appropriate approval of HCC FE/M Director.
3.17. Develop, maintain and communicate the policies and procedures associated with the delivery of efficient and quality operations and maintenance services in support of the various HCC facilities and amenities. Library of Facility drawings, manuals or electronic files will include comprehensive operational manuals, safety programs, emergency procedures (per established college guidelines), building operations and maintenance procedures.
3.18. Provide comprehensive capital planning services associated with infrastructure systems to ensure critical business operations are as free as possible from interruptions due to equipment failures and changing business requirements are accommodated within the infrastructure/operational system’s capacities.
3.19. Provide complete and efficient operational management of all base building infrastructure systems. Ensure all business environments with full 24/7 auxiliary back-up power capabilities are protected from internal and external interruptions. Ensure all business environments without full 24/7 back-up capabilities are free from controllable interruptions.
3.20. Provide complete operational maintenance of underground storage fuel tanks per city, state, and federal codes.
3.21. Maintain potable drinking water systems within designated Facilities and maintain decorative fountains.
3.22. Maintain all plumbing systems and associated components including supply and waste piping.
3.23. Provide the expertise, supervision, maintenance, repair services associated with the various building systems within designated Facilities. Ensure all systems function as designed to maintain system reliability and conserve energy.
3.24. Provide parking facilities maintenance services associated with designated parking garages and surface parking lots to include all associated components of said lots and garages.
3.25. Provide preventive/predictive maintenance and property inspections supporting designated Facilities, including, but not limited to, base building mechanical, electrical, fire/life safety and plumbing systems to keep all in good working order and in compliance with manufacturer’s recommendations and industry best practices.
3.26. Maintain effective customer relations. Develop and implement procedures to define and ensure the prompt handling of remedial work requests, including the proper communication channels and service level response goals.
3.27. Develop and implement 24-hour emergency response and procedures for responding to building alarms and severe weather conditions that affect life safety, physical assets or business operations. Ensure off-hour response to alarm condition procedures include on-site response by certified personnel within one (1) hour of the report to awarded contractor.
3.28. Participate in the review and revision of the emergency response plans as needed and be prepared to execute the support responsibilities identified by those plans.
3.29. Designate a safety officer to coordinate all regulatory, building code, fire and safety requirements and to develop, implement, maintain and communicate to the HCC Safety Director the following:
3.29.1. An effective program supporting all OSHA regulations, regulatory reporting requirements and safety related training requirements.
3.29.2. A safety data sheets program (SDS) for all chemicals used at any site contained within the portfolio under the Contractor’s range of responsibilities.
3.29.3. Safety officer shall correspond and be point of contact for regulatory agency inspections/visits to portfolio.
3.30. Provide service/call center services to receive work requests, process remedial and preventive maintenance work orders and implement emergency and normal response procedures.
3.31. Maintain and tabulate the information required to effectively prepare monthly, quarterly and annual workload, financial and management reports. Develop and administer a process for measuring HCC satisfaction at a discrete business level; analyze results and translate survey results into specific business improvements.
3.32. Provide maintenance services for electronic security equipment repair and maintenance services required at designated properties within the portfolio. Functional components include intrusion alarm systems, CCTV, video surveillance and recording, duress alarm equipment, door contacts, access control system equipment and other electronic equipment and devices.
3.33. HCC is not requiring the use of any specific subcontractor nor are they endorsing subcontractors for this assignment. Proposers are responsible to undertake appropriate due diligence in reviewing and selecting subcontractors and partners for inclusion in their proposal.
3.34. Safety Programs (applies to all services provided).
3.35. Contractor shall provide HCC Managers with copies of its safety program(s) as requested.
3.36. Contractor will be responsible for safety aspects relating to the range of services provided at each Facility.
3.37. Contractor shall ensure that its subcontractors adhere to safety requirements.
3.38. Quality Control Programs (applies to all services provided).
3.39. Contractor shall provide quality improvement monitoring and evaluation programs.
3.40. Contractor shall effectively evaluate the building systems, architectural finishes and products, structure and property to ensure all components are serviced and renewed in a manner that ensures their integrity, appearance and reliability is maintained over the long term and extend useful life.
3.41. Procurement Procedures and Programs (applies to all services provided)
3.42. Contractor shall have a call center and answer phone calls, e-mails, and radio calls in a prompt manner.
3.43. The status of work requests should be communicated to the HCC Managers on a consistent regular basis, as required by the individual HCC Managers.
3.44. Contractor will track client satisfaction levels by conducting semi-annual surveys among the HCC Managers. Copies of the summary results should be sent to the Director of FE/M and the Chief Facilities Officer.
3.45. Contractor shall ensure that appropriate documentation, procedures and manuals are developed, maintained and disseminated.
3.46. Contractor shall utilize facility condition assessments to monitor the operational efficiency and quality of college portfolio as requested by the Director or its designee.
3.47. Contractor will monitor and report on its progress in meeting project oriented objectives as requested.
3.48. Contractor shall provide Additional Work Services—unique or specialized requests outside the base building services—as requested. Contractor shall supply the College with no less than three (3) bid quotations from reputable vendors and submit all information for review and approval by the Director of FE/M. A markup not-to-exceed ten (10) percent shall be allowable to contractor for such work. Once approved by the Director of FE/M, all support information (including all bid quotations) related to any request, shall be provided to the Procurement Operations Department for issuance of an individual Purchase Order. Contractor shall be responsible for ensuring the use of certified Small Businesses Enterprises (SBE) and will be required to report SBE utilization to the Procurement Operations Department monthly.
3.49. Contractor shall develop a methodology to track Additional Work Services work order costs and volumes separately from base building services.
3.50. Contractor should make client satisfaction a priority in providing services under the agreement.
3.51. Contractor's employees should be trained to be customer-service oriented and to positively and politely interact with college employees and the public when performing contract services. Contractor's employees should be clean, courteous, efficient, and neat in appearance at all times and committed to offering the highest degree of service to the public. If, in the Director or its designee’s determination, the Contractor is not interacting in a positive and polite manner with college employees and the public the Contractor shall take all remedial steps to conform to the standards set by the agreement and is subject to termination for breach of contract.
3.52. HCC shall retain the right to request the replacement of the RM/GM and/or the CMMS Representative for reasons HCC deems sufficient.
3.53. The Contractor shall provide for a maintenance management system to apply proven management principles to optimize the use of the contract designated levels of personnel, equipment, material, space, time and funds. The contractor will also:
3.53.1. Provide effective maintenance support and response to HCC administrative and operational requirements. Work schedules or shifts for FTEs will be generated by the contractor and approved by HCC.
3.53.2. Maintain a high level of productivity in the maintenance work force.
3.53.3. Assure a high quality standard for maintenance performance.
3.53.4. Develop operating plans and strategies which ensure that adequate resources are available at all times (24/7/365) to properly support or respond to the scale and technical complexity of the building systems and operational occurrences. This shall include inclement weather, environmental or other events that may disrupt normal day to day operations.
3.53.5. Provide effective communications and coordination with major capital improvement initiatives that are directly managed by other entities.
3.53.6. Achieve cost reductions in performing proper maintenance in HCC facilities. Meeting or exceeding national comparable cost data for this area.
3.53.7. Provide a maintenance program. The Contractor shall advise HCC of maintenance project resource requirements.
3.53.8. Contractor's actions shall respond to HCC's current designation of priorities for the completion of preventive maintenance, corrective maintenance, and predictive maintenance.
3.53.9. Provide HCC with a successful maintenance program that is measurable through weekly inspections with an inspection report signed by HCC designated personnel and the Contractor. Provide monthly preventive maintenance/work order metrics to review with FE/M team. Success will also be monitored through the comments from the College community through a web-based complaint site.
3.53.10. Training - Awarded vendor shall provide, as needed, on-site CMMS training to Houston Community College staff.
3.53.11. Set-up and Implementation - Vendor shall include any costs for set-up and implementation of the software system and in the cost of the operation of the Facility Maintenance software (CMMS).
3.53.12. Vendor shall provide information on software updates annually. Please note frequency of updates, along with any additional cost associated with the upgrade.
3.53.13. Use IFMA standards to sq. ft. staffing ratio of FTEs. To include, but not limited to:
3.53.13.1. Maintenance workforce (Electricians, HVAC and central plant operators, plumbers; controls and low voltage, stationary engineers, Other FTE's)
3.53.13.2. Maintenance Management (Group Supervisors, Operation and or maintenance managers)
3.53.13.3. Administrative support (Help Desk Staff, Administrative Assistant, Customer Services Representatives)
3.53.13.4. Total Maintenance Staff (shall be included in this contract)
3.53.13.5. Exclusions: General Maintenance, Locksmith and Landscaping
4. Electrical, Mechanical and Elevator System Maintenance Services
Electrical maintenance and repair up to $10,000 will be the responsibility of contractor under this contract. Any electrical systems services that shall be the responsibility of the college, could be addressed by way of task of work (TOW) process which; shall be on an as needed/requested basis (ancillary service). Electrical maintenance to include but not limited to annual electrical panel maintenance that entails visual inspection as well as verification of tight and correct terminations. Thermal imaging to be performed only on motor control assemblies that contain operating equipment of 100 amps or more per circuit. Thermal imaging will be incorporated for preventive maintenance except where needed for diagnostic services.
4.1. Electrical and mechanical systems maintenance services includes parts, predictive, preventive and corrective maintenance for all electrical, mechanical and elevator systems including but not limited to the following list of systems:
4.2. Primary Power Systems:
4.2.1. Transformers
4.2.2. Main switchgear
4.2.3. Wiring
4.2.4. Weather heads
4.2.5. Sub-stations
4.2.6. Annual infrared testing of panels
4.3. Secondary Power Systems:
4.3.1. Switchgear
4.3.2. Motor control centers
4.3.3. Motor starters
4.3.4. Disconnects
4.3.5. Panel boards
4.3.6. Circuit breakers
4.3.7. Transformers
4.3.8. Computer distribution units
4.3.9. Wiring Devices
4.3.10. Receptacles Accessories
4.3.11. UPS
4.3.12. Automatic doors
4.4. Lighting Systems:
4.4.1. Panel boards
4.4.2. Circuit breakers
4.4.3. Transformers
4.4.4. Lighting relays and controls
4.4.5. Infrared and ultrasonic sensors
4.4.6. Photocells
4.4.7. Lighting dimmer controls
4.4.8. Light fixtures
4.4.9. Emergency lighting
4.4.10. Parking lot lights
4.4.11. Wiring Switches Accessories
4.4.12. Interior and exterior LED signage and communication
4.4.13. Emergency Blue Phones
4.5. Uninterrupted Power Unit System:
4.5.1. Batteries
4.5.2. Transfer switches
4.5.3. Wiring devices and accessories
4.5.4. Annual inspection and major overhaul
4.6. Potable and Non-Potable Water Systems:
4.6.1. Water detention pond pumps
4.6.2. Pumps
4.6.3. Filters
4.6.4. Softeners
4.6.5. Hot water heaters
4.6.6. Isolation valves
4.6.7. Piping
4.6.8. Purifiers
4.6.9. Sewage pumps
4.6.10. Fixtures
4.6.11. Controls and related plumbing components
4.7. Emergency Power Generators:
4.7.1. Diesel and natural gas engines Motors
4.7.2. Pumps
4.7.3. Generator
4.7.4. Switchgear
4.7.5. Wiring
4.7.6. Oil sampling and rectification
4.7.7. Transfer Switches and Controls
4.8. Exclusions: Interior bulb replacement shall be the responsibility of college staff up to 20 feet.
4.9. FUEL - Annual inspection of fuel storage tanks in accordance with (EPA/TCEQ) guidelines. Record keeping for UST shall be in accordance with all city, state, and federal code. Contractor will perform regular testing of the fuel and provide chemical rectification to restore fuel to ideal performance levels. Fuel filtration techniques are employed when fuel has water and/or sediment levels that exceed ASTM standards or when microbiology growth is detected. Completed forms are to be sent to the Safety Department. Exclusion: Client shall provide fuel.
4.10. It is the intent of this contract for all electrical components be maintained by the contractor. All-inclusive service shall be expected under the terms of this contract.
5. ELEVATOR, ELEVATOR EQUIPMENT AND WHEELCHAIR LIFT SERVICES
5.1. Elevator Service maintenance and repair is included up to $10,000 on all current elevator equipment, elevators and wheel chair lifts and other associated components of the conveyance systems are included.
5.1.1. Traction Elevators;
5.1.2. The Contractor shall provide a preventive maintenance program to deliver service tailored to the buildings specific needs. Equipment type, component life, equipment usage, and building environment will be taken into account when planning routine short and long term maintenance schedules and records for each elevator. The units will be provided with devices to monitor equipment usage. Industry Standard work processes will be used.
5.1.3. All equipment, materials and installation shall conform to: ANSI the American National Standard Safety Code for Elevators, Dumbwaiters, Escalators, and Moving Walks, American Standard Practice for the Inspection of Elevators, Inspectors Manual, and National Fire Protection Association (NFPA) code. The Contractor will be trained, licensed personnel directly contracted and supervised maintenance contractor. The contractor will be qualified to ensure the equipment is properly adjusted, and they will use all reasonable care to maintain the elevator equipment in proper and safe operating condition.
5.1.4. The Contractor will regularly and systematically examine, adjust, lubricate as required, and if conditions warrant, repair or replace, but not limited to:
5.1.4.1. Machine, worm gear, thrust bearings, drive sheave, drive sheave shaft bearings, brake pulley and brake coil, contact, linings and component parts.
5.1.4.2. Motor and motor generator, motor windings, rotating element, commutator, brushes, brush holders and bearings.
5.1.4.3. Silicon control rectifier, reactors, filters, heat sinks, amp traps, transducers and all control components.
5.1.4.4. Controller, selector and dispatching equipment, all relays, solid state components, resistors, condensers, transformers, contacts, leads, dash pots, timing devices, computer and micro computer devices, steel selector cable or tape and mechanical and electrical driving equipment.
5.1.4.5. Governor, governor sheave and shaft assembly, bearings, contacts and governor jaws.
5.1.4.6. Deflector or secondary sheave, bearings, car and counterweight guide rails, top and bottom limit switches, governor tension sheave assembly, compensating sheave assembly, counterweight and counterweight guide shoes including rollers and gibs.
5.1.4.7. Hoist way door interlocks and hangers, bottom door guides and auxiliary door closing devices.
5.1.4.8. Automatic power operated door operator, car door hanger, car door contact, door protective device, load weighting equipment, car frame, car sling, car safety mechanism, platform, wood platform flooring, elevator car guide shoes, gibs or roller and call buttons
5.1.5. The Contractor will also:
5.1.5.1. Examine monthly all safety devices and governors and conduct annual no-load test, and each fifth year perform a full-load, full-speed test of safety mechanism, overhead speed governors, car and counterweight buffers. The car balance will be checked and the governor set. If required, the governor will be calibrated and sealed for proper tripping speed.
5.1.5.2. Load weighing devices will be calibrated after annual and five year safety tests.
5.1.5.3. Renew and wire ropes as often as necessary to maintain an adequate factor of safety; equalize the tension on all hoist and compensation ropes, and shorten ropes and chains as required to provide legal and reasonable bottom clearances.
5.1.5.4. Repair or replace conductor cables and hoist way and machine room elevator wiring as required.
5.1.5.5. Furnish lubricants and hydraulic fluid compounded to the Utilities Contract Coordinator copies of the S.D.S. for all materials stored on- site. The Contractor shall also maintain, and if conditions warrant, repair or replace the following auxiliary equipment with the Director of FE/M and Administration or designee's prior approval.
5.1.5.6. Check emergency lighting, batteries, trickle charger and related wiring and Components weekly.
5.1.5.7. Check Elevator Management Systems, Consoles, CRT's keyboards, wiring and components and all other devices associated with these systems. (Only those systems and devices directly related to Elevator Communication) weekly.
5.1.5.8. Check Fire Emergency Operation and elevator operating devices (Only those systems and devices directly related to the Elevator System) weekly.
5.1.5.9. Check Emergency Power Operation and elevator operating devices (Only those systems and devices directly related to the Elevator System) weekly.
5.1.5.10. Check all handicap devices that are part of the elevator system.
5.1.5.11. Check all elevator related earthquake devices.
5.1.5.12. Inspect emergency communication devices for elevator to ensure devices are working properly weekly.
5.1.6. Vendor shall display maintenance logs within elevator equipment room in a protective binder in a conspicuous location.
6. Hydraulic Elevators and Wheelchair Lifts
6.1. The Contractor shall provide a preventive maintenance program to deliver service tailored to the building specific needs. Equipment type, component live, equipment usage, and building environment will be taken into account when planning routine short and long term maintenance scheduled records for each elevator. The units will be provided with devices to monitor equipment usage, Industry Standard work processes will be used.
6.2. All equipment, materials and installation shall conform to: ANSI, standards The American National Standard Safety Code for Elevators, Dumbwaiters, Escalators, and Moving Walks, ANSI, American Standard Practice for the Inspection of Elevators, Inspectors Manual, and National Fire Protection Association (NFPA) code. The Contractor will use trained, licensed personnel directly contracted and supervised by them. The contractor will be qualified to ensure the equipment is properly adjusted, and they will use all reasonable care to maintain the hydraulic elevator equipment in proper and safe operating condition.
6.3. The Contractor will regularly and systematically examine, adjust, lubricate as required, and if conditions warrant, repair or replace, but not limited to:
6.3.1. Pumps, pump motors, operating valves, valve motors, motor winding, leveling valves, plunger, plunger packing, exposed piping and hydraulic fluid tanks.
6.3.2. Controller, leveling devices and cams, all relays, magnet frames, solid state components, resistors, condensers, transformers, contacts, leads, timing devices, resistance for operating and motor circuits, operating circuit rectifiers.
6.3.3. Hoist way door interlocks, hoist way door hangers, bottom door guides, auxiliary door, auxiliary door closing devices and hoist way switches.
6.3.4. Automatic power operated door operator, car door hanger, car door contract, door protective device, car frame, car ventilation system, platform, wood platform flooring, in the elevator car, car guide, rails, car guide shoes, gibs or rollers. Filters, mufflers and muffler components.
6.4. The Contractor will also
6.4.1. Examine monthly, all safety devices and conduct pressure tests and other tests required by ANSI standards or other applicable city, state, and federal codes.
6.4.2. Repair or replace conductor cables, elevator hoist way wiring and machine room elevator wiring.
6.4.3. Furnish lubricants and hydraulic fluid compounded to the manufacturer's rigid specifications. Contractor will furnish the Director of FE/M or designee copies of the S.D.S. for all materials stored on-site.
6.4.4. In accordance with the manufacturer's specifications, conduct an analysis hydraulic fluid to detect contaminants and assure proper viscosity and make necessary corrections and replace fluid as required. A copy of the findings shall be furnished to the Director of FE/M or designee within thirty (30) calendar days of the analysis.
6.4.5. Clean excessive fluid leakage from pump pans, cylinder heads, machine room and pit floors, The Contractor from pump pans, cylinder heads, machine room and pit floors. The Contractor shall also maintain, and if conditions warrant, repair or replace the following auxiliary equipment with the Director of FE/M and Administration or designee prior approval.
6.4.6. Check emergency lighting, bulbs, batteries, trickle charger and all related wiring and components weekly.
6.4.7. Check Elevator Management Systems, Consoles, CRTs keyboards, wiring and components and all other devices associated with these systems. (Only those systems and devices directly related to Elevator Communication) weekly.
6.4.8. Check Fire Emergency Power Operation and elevator operating devices (Only those systems and devices directly related to the Elevator System) weekly.
6.4.9. Check Emergency Power Operation and elevator operating devices (only those systems and devices directly related to the Elevator System) weekly.
6.4.10. Check all handicap devices that are part of the elevator system.
6.4.11. Check all elevator related earthquake devices.
6.4.12. Inspect emergency communication devices for elevators to ensure devices are working properly weekly.
6.5. Test and Reports, but not limited to
6.5.1. Yearly inspection and report: The Contractor shall conduct, and annual, non-load, low speed test of elevator car and counter weight safeties, a test of buffers and safety device tests and a hydraulic elevator pressure relief valve test as required by ANSI code. Every fifth year, the Contractor shall conduct a rated load, rated speed safety test and a test of governor's safeties and buffers. The result of each test shall be delivered to Director of FE/M or designee in writing within fourteen (14) days of completion date of the test.
6.5.2. Annual performance evaluation and report: The Contractor shall conduct annual evaluations of elevator performance, including car speed, door operations, riding quality, car leveling, floor to floor time and system operation, including traffic handling response time and step indexing. The result of the evaluation and report shall be delivered to Director of FE/M or designee in writing within thirty (30) days of test.
6.5.3. Contractor Reports - Operation problems: The Contractor shall maintain schedules, operations logbooks, inventory lists, equipment specifications and drawings, which describe the elevator installations covered by these specifications and the services performed. These documents shall be made available to Houston Community College (HCC) and review quarterly with Director of FE/M.
6.5.4. Contractor shall be required to obtain a computerized operations verification service to test on a weekly basis two-way emergency communication. A report shall be submitted on a weekly basis to the Director of FE/M or designee. Emergency two-way communication issues shall be addressed immediately.
6.6. Personnel Qualifications
6.6.1. Only qualified and licensed service technicians shall be used to perform repairs and maintenance services stipulated in this Scope of Services. Service Technicians assigned by the Contractor must be fully qualified in all aspects of maintenance to be performed, including repairs that may become necessary during the term(s) of this contract.
6.6.2. The Contactor shall have and maintain sufficient backup technicians who are qualified in all aspects of equipment repair and services requirements to assume the responsibilities for the maintenance of the included elevator systems in case of emergency or other unforeseen conditions.
6.7. Working Hours and Response Time
6.7.1. Routine Services: All routine work shall be performed during regular working hours between 8:00 a.m. to 5:00 p.m., Monday through Friday, holidays excluded. The Contractor shall respond to requests for services within one (1) hours of being notified of a service request during regular working hours. The Contractor shall respond within two (2) hours during other than regular working hours and days. Note: "Response" shall mean that a "qualified technician" shall be on the job site and prepared to work within the response time frames specified herein, after notice is given to Contractor by HCC. The Contractor shall respond (in person) to requests for emergency services within one (1) hour of being notified by HCC that an emergency exists except when a person is stuck in an elevator. In such case, the response time shall be no longer than thirty (30) minutes. Emergency services shall be provided twenty-four (24) hours a day, seven (7) days a week, holidays included.
6.8. Callback Services or Emergency Services: The Contractor shall provide 24-hour callback service to take care of minor and/or major elevator malfunctions occurring between scheduled maintenance services. The call back response times shall be immediate during regular hours and thirty (30) minutes during other than regular hours. All overtime work shall require prior approval from the HCC Manager or Contract Administration.
6.8.1. It is the intent of this contract for all elevator components be maintained by the contractor. All-inclusive service shall be expected under the terms of this contract.
7. HVAC SYSTEMS MAINTENANCE SERVICES
7.1. HVAC maintenance and repair up to $10,000 will be the responsibility of contractor under this contractor. All HVAC system services that shall be the responsibility of the college could be addressed by way of task of work (TOW) process which shall be on an as needed basis. HVAC maintenance to includes but not limited to annual chiller preventive maintenance services of one (1) annual oil analysis, tube cleaning, vibration report, and general efficiency checks and adjustments. Reciprocating chiller to include one (1) annual oil analysis, efficiency check and adjustments. These specified services as listed are in addition to all other normal preventive maintenance tasks as scheduled. Water treatment and filter replacement is included in these services. All filters shall be dated at installation. All associated HVAC components are included, along with air intakes, registered louvers and return grills.
7.2. The Contractor shall furnish labor, tools, equipment, transportation and supervision necessary for the maintenance, inspections and repairs to aid conditioning, heating, and ventilating systems located in the various buildings listed in the attached schedules. All materials, system components, refrigerant, lubricants and parts necessary for routine preventive maintenance in repair heating, ventilating and air conditioning units shall be supplied by the Contractor.
7.3. The Contractor shall replace worn or failed components and parts. All replacement parts will be of like or current design to minimize system depreciation obsolescence.
7.4. The Contractor shall perform complete maintenance service, inspections, and emergency calls for all equipment Included under this Scope of Services. This service shall consist of thorough maintenance work in accordance with the best commercial practice governing the maintenance of air, heating and ventilating systems in accordance with the best commercial standards.
7.5. The services shall include Routine Preventive Maintenance, Multi-Year Major Stop Maintenance, and Miscellaneous and Emergency Service and Repairs as outlined below.
7.6. Manufacture Startup checklist, monitoring and completion forms complete with any major repairs on HVAC system. Completed Forms presented to Director of FE/M.
7.7. All work shall comply with all city, state, federal, and industry standards.
7.8. Routine Preventive Maintenance Defined: Such service shall include regularly scheduled maintenance tasks and inspections for each unit listed herein. The maintenance tasks and inspection shall consist of, but not limited to, furnishing of all labor, equipment, parts, materials and tools necessary to perform a thorough servicing of all integral parts, oiling, adjusting, protective painting and replacing of all parts where needed to keep the unit in continuous operating condition.
7.9. The following is a non-exhaustive list of services to be performed as part of the Routine Preventive Maintenance to include but not limited to:
7.9.1. Heat exchanger coil replacement shall be the Contractor's responsibility.
7.9.2. Air conditioning water chiller either of centrifugal or reciprocating design: it’s the Contractors responsibility to repair and/or replace all associated components as a result of the tube damage and shall restore equipment to complete and full operating conditions.
7.9.3. Boiler equipment is to be completely inspected, repaired and restored to normal operating conditions. Deficiencies shall be reported to Houston Community College.
7.9.4. Components excluded from specification are: insulation, casings, boiler settings, shell cast sections of sectional boiler and connection nipples, baffles, walls stays and straps, fire boxes and refractory, access and inspection doors.
7.9.5. Filter change and coil cleaning shall be the responsibility of the Contractor. Filters are Filter grade to be replaced at a minimum of 90-day intervals. A report detailing each unit whose filters have been replaced shall be submitted monthly.
7.9.6. Cooling tower responsibility shall be to the responsibility shall be to the following components: motor, belts, pulley or gearbox, float control and valve sump screen, spray nozzles: Tower mechanical maintenance only. This excludes structure, piping, basin and all other components within tower.
7.9.7. Valves associated with the HVAC system is the responsibility of the Contractor to repair and/or replace as a part of this Routine Preventive Maintenance schedule.
7.9.8. Chemical treatment of chill water, condensing water, and hot water systems.
7.10. Multi-Year Major Stop Maintenance Defined: Major stop maintenance shall be classified as long-range preventive maintenance and shall be performed at intervals greater than one year and less than three years. The intervals of the Multi-Year Major Stop Maintenance shall be determined by the Contractor and HCC's Director of FE/M best judgment based on equipment applications, operating hours, age and routine preventive inspection results. The Multi-Year Major Stop Maintenance shall include major internal maintenance to inspect, repair and/or replace those parts and/or components whose normal wear indicated repair or replacement is needed including all necessary maintenance tasks to perform internal cleaning, clearance adjustments, bearing maintenance, shaft maintenance and those preventive maintenance tasks that are required to keep equipment in good operating condition.
7.11. General Maintenance: HVAC systems maintenance includes parts, predictive, preventive and corrective maintenance including, but not limited to the list of systems. The Contractor must define what HVAC systems are included in the preventive and corrective maintenance.
7.12. Schedule of Work: It shall be the Contractor's responsibility to notify HCC's representative in writing before scheduling Multi-year Major Stop Maintenance or other maintenance repairs requiring a shutdown of systems so as to coordinate with HCC's schedule. It shall also be the Contractor's responsibility to provide advance written notification to HCC of any Miscellaneous and Emergency Services and Repairs needed to be performed that are in addition to the Routine Preventive Maintenance. The HCC representative must authorize these additional services.
7.13. It is the intent of this contract for all HVAC components be maintained by the contractor. All-inclusive service shall be expected under the terms of this contract.
8. BUILDING AUTOMATION SYSTEM (BAS), BUILDING ENERGY MANAGEMENT SYSTEM (BEMS), BUILDING SECURITY SYSTEM (BSS) AND FIRE LIFE SAFETY EQUIPMENT (FLSE) MAINTENANCE SERVICES
8.1. BAS/EMS/BSS service to include energy management monitoring, adjustments and repair up to $10,000.
8.2. BAS/ BSS/ BEMS Monitoring and Service covers the requirements for the Contractor to provide Building Automation System (BAS) and Building Security System (BSS) monitoring and service:
8.2.1. The Contractor shall also support a reporting system that includes both written and online formats.
8.2.2. Contractor shall provide, but not limited to, all supervision, labor, materials, spare parts, supplies, equipment and services, whether or not specifically mentioned in these documents, to operate and maintain the Building Automation System and Building Security System, its associated components (including cameras), controls and instrumentation on a continuous basis 24 hours per day, 7 days per week, 365 days per year.
8.3. Systems Management Program The following services shall be provided for each of the campuses listed in the Facility Maintenance Information:
8.3.1. Preventive Maintenance Program Building Automation quarterly: The Contractor shall perform a scheduled inspection during regular business hours components at each campus. Upon conclusion of inspection, a report shall be generated describing problems or defective parts and a plan of action to repair or replace all failed parts shall be developed and submitted to HCC.
8.3.2. Preventive Maintenance Program Building Security quarterly: The Contractor shall perform a scheduled inspection during regular business hours of the particular HCC facility to verify operation and calibration of all BSS components at each campus. Upon conclusion of inspection, a report shall be generated describing problems or defective parts and a plan of action to repair or replace all failed parts shall be developed and submitted to HCC.
8.3.3. Energy Conservation Programs: The Contractor shall inspect system operations at each site and recommend improvement that may promote the conservation of energy, reprogramming of sequences shall be included by the contractor.
8.3.4. Remedial Maintenance: The Contractor shall respond within one (1) hour to malfunctions that impact the facility's temperature or access control.
8.3.5. Help Desk and Service Call Response Plan: All BAS & BSS service requests shall be handled and co-coordinated by the help desk. The Contractor's help desk shall trouble shoot the problem via the building automation workstations. If the problem cannot be solved from remote workstation then a technician shall be dispatched to the jobsite. All service requests/responses shall be stored and made available to the Building Maintenance Supervisor and the Director of FE/M.
8.3.6. Replacement Parts: All replacement parts shall be new and have the same manufacturer as original parts and shall be locally inventoried.
8.3.7. Systems Hardware and Software: The Contractor shall maintain all BAS and BSS hardware, firmware and software in a complete and totally operational condition. The Contractor shall guarantee all BAS and BSS hardware, software and firmware for a period of one (1) year from the date of installation.
8.3.8. Staffing and Operator Qualifications: The Contractor shall maintain a minimum of three (3) technically qualified service operators to receive BAS and BSS service requests.
8.3.9. Monitoring Center: All campuses should be monitored via remote workstations located at the Contractor's office. All major equipment shall be verified to be functioning within normal parameters. Any major equipment found not functioning properly should be reported to HCC as well as to Director of FE/M or designee. All alarms shall be received and logged at the monitored workstations and appropriate action taken to rectify alarm conditions within two (2) hours.
8.3.10. Reports: Contractor shall submit a monthly report to HCC containing an overall summary of maintenance work performed during the month, the results of tests conducted and all service requests. This report shall also be available online.
8.3.11. Routine Operations:
8.3.11.1. Data Backup: The Contractor shall provide two (2) complete system data backups of each site quarterly. The data backup shall include backing up all field panels to the Workstation.
8.3.11.2. Phone Support: The Contractor shall provide technically qualified phone support, which shall be available to HCC personnel on a 24-hour basis. This provides support for HCC personnel and contractors with trouble shooting and diagnosing of HVAC control problems. The service desk shall have a building automation workstations dedicated to the HCC. These workstations shall allow the service desk to provide real time information and support for all BAS & BSS building operations.
8.3.11.3. Service Desk: The Contractor’s service desk shall be the first point of contact for all BAS & BSS requests i.e. but not limited to: scheduling, hot/cold calls, no video, no access, etc.
8.3.11.4. Experienced building operators with BAS Controls.
8.3.11.5. All requests and inquiries shall be logged and tracked. Any authorized user via a HCC workstation net browser may submit requests. Also the status of previously submitted requests shall be available upon request. If a workstation is not available, the service desk may be contacted by web phone or fax between normal operating hours and scheduling requests submitted. Service desk normal hours shall be 8:00a.m. to 5:00p.m. and shall be manned for this time period.
8.3.12. It is the intent of this contract for all BAS/BSS/BEMS components be maintained by the contractor. All-inclusive service shall be expected under the terms of this contract.
9. FIRE LIFE SAFETY EQUIPMENT (FLSE) MAINTENANCE
9.1. Fire systems will be included regarding suppression and notification maintenance and repair up to $10,000. Maintenance tasks and associated inspections per governing body regulation and having jurisdiction will be included for all systems currently "blue tagged" by the Fire Marshall.
9.2. Contractor shall devise a plan to immediately address "yellow tag" and "red tag" situations. In addition, fire alarm monitoring will be included under these services. HCC shall be notified immediately of any and all active alarms within portfolio (list of contacts shall be provided).
9.3. The Contractor shall maintain and repair Fire Alarm & Fire Suppression Systems at listed HCC facilities.
9.4. The contractor awarded this contract shall provide the necessary tools, equipment and staff to maintain, repair, and monitor the alarm system and notify the appropriate authority having jurisdiction.
9.5. The Contractor shall conform to all NFPA and NEC codes and standards may apply to include all city, state, and federal regulation codes. It shall be the contractor’s responsibility to maintain full compliance with any and all fire code or regulations that apply to the college. This includes annual and monthly inspections of fire extinguishers in accordance to current NFPA standards.
9.6. The Contractor's personnel shall be qualified and experienced in the inspection, testing, maintenance, and repair of the fire alarm and fire suppression systems. Qualified personnel shall be, but not limited to, individuals with the following qualifications:
9.6.1. Factory trained and certified
9.6.2. Licensed (not Certified) by the National Institute for Certification in Engineering Technologies - Fire Alarms
9.6.3. Certified by the State of Texas or local authority
9.6.4. Trained and qualified personnel employed by an organization listed by a national laboratory for the services of fire alarm systems
10. EMERGENCY SERVICES/CALL OUTS FOR FIRE ALARM SYSTEMS:
10.1. The Contractor shall provide on-call "Emergency Services" 24 hours per day, seven days per week 365 days per year.
10.2. The Contractor shall provide emergency service in response to a telephone request by an HCC representative within one (1) hour. The qualified person shall be accessible by telephone 24/7/365.
10.3. Contractor shall be required to obtain 24/7/365 third-party monitoring service for any and all fire life safety components within the College portfolio.
11. SYSTEM DEVICES REQUIRING SERVICES AND INSPECTION:
Maintenance, testing, inspection, repair and/or replacement shall be, but not limited to the following equipment and associated components:
11.1. Fire and Smoke Detection Equipment:
11.1.1. Fire detectors
11.1.2. Smoke detectors
11.1.3. Manual pull stations
11.1.4. Alarm bells and lights
11.1.5. Annunciators
11.1.6. Speakers, flow detectors
11.1.7. Flow switches
11.1.8. Valve switches
11.1.9. Wiring
11.1.10. Devices
11.1.11. Accessories
11.2. Fire Suppression Systems:
11.2.1. Fire pumps and controls
11.2.2. Jockey pumps
11.2.3. Sprinklers (wet/dry)
11.2.4. Fire hose cabinets/racks
11.2.5. Manual fire extinguishers
11.2.6. Piping valves
11.2.7. Accessories
11.2.8. Portable suppression devices
11.2.9. NFPA 25 " Chum test "
11.3. Halon Fire Extinguishing System:
11.3.1. Halon storage tanks
11.3.2. Manual pull stations
11.3.3. Abort switches
11.3.4. Alarm bells and lights
11.3.5. Control panels
11.3.6. Annunciators
11.3.7. Speakers
11.3.8. Piping
11.3.9. Valves
11.3.10. Wiring
11.3.11. Devices and accessories
11.4. FM 200 Extinguishing Systems:
11.4.1. FM 200 storage tanks
11.4.2. Manual pull stations
11.4.3. Abort switches
11.4.4. Alarm bells and lights
11.4.5. Control panels
11.4.6. Annunciators
11.4.7. Speakers
11.4.8. Piping
11.4.9. Valves
11.4.10. Wiring
11.4.11. Devices
11.4.12. Accessories
11.5. It is the intent of this contract for all System Devices and all associated components be maintained by the contractor. All-inclusive service shall be expected under the terms of this contract.
12. OTHER INFORMATION
12.1. As used in this Agreement, the following terms are defined as follows:
12.2. Preventive Maintenance:
12.2.1. Any planned maintenance activity that is designed to improve equipment life and avoid any unplanned maintenance activity.
12.2.2. The Contractor shall schedule preventive maintenance tasks by Computerized Maintenance Management System (CMMS) to assure a uniform and detailed but not limited to the following, but not limited to:
12.2.2.1. Inspections
12.2.2.2. Lubrications
12.2.2.3. Tests
12.2.2.4. Adjustments
12.2.2.5. Corrective maintenance tasks found during preventive maintenance
12.2.3. A discussion of the organization of essential elements of an effective program is as follows, but not limited to:
12.2.3.1. Work instructions
12.2.3.2. Work inventory
12.2.3.3. Work Assignments
12.2.3.4. Basic records
12.3. It is the intent of this contract for all FLSE components be maintained by the contractor. All-inclusive service shall be expected under the terms of this contract.
12.4. Condition Based Maintenance is performing inspections in a real-time mode. Inspection in real-time mode is identified using the trending methodology. Trending includes sensors installed in equipment that sends signals indicating maintenance needs to be scheduled and performed. Trending also allows technicians to read or trend the information to avoid unnecessary or erroneous maintenance schedules.
12.5. Random Failures are any failure that occurs without notice or warning.
12.6. Normal Wear Out is a type of failure that can be designed in a preventive maintenance program. Designed to prolong or prevent and these types of failures occur progressively over a relatively long period of time. The PM Management Team should design programs to spot signs of wear and take appropriate measures to correct the situation.
12.7. Mandatory Preventive Maintenance are those that must be performed at all costs when they are due. They may involve, but not limited to, OSHA, safety, EPA and license inspections as well as state and local inspection requirements among others. This shall follow any and all city, state, and federal codes/requirements.
12.8. Non-Mandatory preventive maintenance are inspections or service PMs that can be postponed for a short time period or even eliminated for the present cycle without resulting in immediate failure or performance penalty. Each PM task should be designated in one of these categories.
12.9. Inspections will involve filling out a maintenance request time ticket and then creating work orders to cover any problems discovered during the inspection.
12.10. Task-oriented preventive maintenance allow the individual performing the PM to take time to make minor repairs or adjustments, eliminating the need to write some of the work orders when turning in the inspection sheet. For scheduling purposes, a time limit shall be set on how long each task should take. The Contractor shall set time limits for each type of PM task for each critical piece of equipment.
12.11. Operator Time Loss - shall include but is not limited to the following:
12.11.1.1. Time to report the failure
12.11.1.2. Time for maintenance to arrive
12.11.1.3. Time for maintenance to make repairs
12.11.1.4. Time to restart the equipment
12.12. Maintenance Costs - shall include but not limited to the following:
12.12.1.1. Time to obtain the equipment
12.12.1.2. Time to repair the equipment
12.12.1.3. Time to dispatch staff to area
13. CONTRACTOR RESPONSIBILITIES
13.1. Administrative and Technical Direction
13.1.1. The Contractor shall provide, but not limited to, administration and technical direction in the management of the plant operations and maintenance organization. In the discharge of their responsibilities, the Contractor shall be guided by the highest professional technical standards.
13.1.2. The Contractor shall establish and/or maintain records of employees to facilitate the measurement of individual progress, and for preparation of performance reports and to assure that the Contractor’s or HCC employees are working in the best interest of HCC.
13.1.3. The Contractor shall supervise all maintenance skilled employees as shown in the Contractor’s proposed plant operations and maintenance organization plan.
13.1.4. Contractor shall follow Industry Standard Operational Procedures:
13.2. Objectives -The Contractor shall design and implement, with the concurrence of HCC's Facilities Department Standard Operational Procedures. These procedures shall be to, but not limited to, coordinate efforts, skills, and other designated resources through the establishment of clearly defined objectives. The primary objectives shall include a functional, safe environment, and the ability to provide the designated levels of plan environment and maintenance.
13.2.1. Management Systems - The Contractor shall provide clearly defined routines, record requirements, reports, tests and inspections, plant operating instructions and administrative procedures essential to the designated levels of plant operations and maintenance.
13.2.2. Research - The Contractor shall provide the research necessary to design and implement the respective plant operations and maintenance levels and programs.
13.2.3. Direction The Contractor shall develop and maintain a Departmental Maintenance Procedures Manual containing instructions on how each scheduled preventive maintenance task should be performed. All preventive maintenance tasks should be logged into a Centralized Computer Management System (CMMS). Preventive routine tasks shall be generated by the CMMS on a weekly basis and submitted to the appropriate Maintenance Supervisor at each individual College.
13.2.4. Scheduling - The Contractor shall control scheduling the interval of preventive maintenance and task function to be performed by both calendar periods and operating hours as applicable to each piece of equipment. The Contractor is to supply written procedures for each piece of equipment based on equipment manuals.
13.2.5. Inventory/Tools - The contractor shall have inventory in stock for each building for general repairs. Contractor shall not wait until repair is required and procurement of materials thereafter. The Contractor shall provide tools to employees for general repairs and trade specific repairs.
13.2.6. Boiler operation permits- The contractor shall ensure that each HVAC and central Plant operator adhere to the City of Houston Uniform Mechanical Code regulations and any other state or federal regulation that may apply on Boiler Operator Licensing and annual boiler operation inspection. Annual Boiler fee will be the responsibility of HCC.
13.2.7. The contractor shall adhere to all OSHA safety standards for labor, as well as storage of hazardous materials.
13.2.8. Contractor shall post all permits associated with any equipment or system in accordance with state, city, and federal codes/regulations.
13.3. Professional Management
13.3.1. The Contractor's plant operations and maintenance resources of the contractor shall be applied to serve the plant operations and maintenance management needs of HCC. The Contractor shall seek to enhance departmental coordination and cooperation as it related to plant operations and maintenance.
13.3.2. The Contractor shall provide professionally qualified resident and resource management for the performance of plant operations and maintenance administrative engineering functions as defined by the Association of Physical Plant Administrators (APPA).
13.3.3. The Contractor shall make initial and continuing recommendations for the plant operations, maintenance and organization structure, procedures implementation and resource application. The recommendations are to be acted upon only with the concurrence and approval of Director of FE/M or designee.
13.3.4. The Contractor shall provide the leadership necessary for the effective coordination of plant operation and maintenance efforts and skills for proper operation of equipment.
13.3.5. The Contractor shall be required to serve the entire System, which includes all campus locations.
13.4. Personnel Selection and Development
13.4.1. The Contractor and HCC recognizes that the most important element of a successful plant operation and maintenance program is staff or employees hired. The Contractor shall maintain a staff of capable employees thoroughly trained and qualified in the work assigned to them.
13.4.2. The Contractor's personnel policies shall be consistent with the state, city and federal laws.
13.4.3. The Contractor shall consult with HCC as to the selection of the RM. In addition, the Contractor shall submit on a monthly basis an organization chart with the prospective employees that shall be employed at HCC to include the following:
13.4.3.1. Name
13.4.3.2. Craft type
13.4.3.3. Wage rate
13.4.3.4. Certification (Apprentice, Journeyman, Master Electrician, etc.)
13.4.3.5. Years of experience
13.5. Employees – all employees will be on the Contractors or subcontractors payroll.
13.6. Criminal Background Checks - the Contractor(s) shall perform a criminal background check on each employee who services HCC and has reason to visit any HCC campus or facility. Criminal background checks must be performed on an annual basis and all information regarding the criminal background check must be maintained by the contractor and made available to HCC upon request of the Director of FE/M.
13.7. Direction - the Contractor shall encourage employee self-development by establishing clearly defined objectives and uniformity of efforts. There shall be a current, written organizational plan, approved by HCC, for coordination within the department and with other departments. Job descriptions, organizational diagrams, lines of communication and standing orders shall be provided to contribute to employee understanding and teamwork.
13.8. Benefits Package - the Contractor shall submit its benefits package, including but not limited to, Holiday Schedule, Vacation and Sick Leave policies to the Director of FE/M.
13.9. Training - the Contractor shall provide HCC a plan necessary for (or to promote) personal and occupational growth to contracted employees. The program shall include the determination of employee qualifications and experience, on-the-job training, educational counseling. A series of self-study courses shall be made available to the employees. The Contractor must have a company-wide, in-place comprehensive technical training program to include formal skill level upgrade training, recurring training, refresher training and remedial training. The training program must include formal training courses and on-the-job training.
13.10. Identification - all employees must be readily identifiable to the HCC community by uniform and other easily identifiable insignia. Identification badge must be visible.
13.11. Demeanor - employees are expected to be the ambassadors of HCC and should be customer focused.
13.12. Experience - the Contractor must have experience in the provision of on-site management and operations for maintenance.
13.13. Employee Replacement
13.13.1. The Contractor must have a substitute readily available from a pool of qualified staff in the event the Contractor's employee is absent. This substitute would perform the normal duties of the absentee.
13.13.2. Project Management assignment must be approved by Director of FE/M or designee and any replacement personnel must meet the same rigorous standards and certification requirements as contained in the Personnel Selection and Development section of this RFP.
13.14. Total Quality Management (TQM) - the Contractor must have a company-wide TQM program that includes training and participation of all its employees.
13.15. Safety Program
13.15.1. The Contractor and subcontractor shall have a company safety program that addresses the hazards associated with the scope of services requested. The Contractor hired must maintain compliance at all times with all local, state and federal laws and/or regulations with regard to use, storage and disposal of the chemicals or other hazardous materials used during their services performed at an HCC location.
13.15.2. All Contractors and its Subcontractor(s)/Supplier(s) are required, under the Texas Hazard Communication Act to provide Safety Data Sheets (SDS) for all chemicals used or stored on HCC facilities to the Safety Department and upon request.
13.15.3. Chemicals and/or other materials left behind by any vendor after services are completed will be required to be removed and disposed of by the Contractor. HCC is not responsible for the disposal of waste materials left on HCC properties by any contracted vendors.
13.16. Technical Library - the Contractor shall maintain a technical library consisting of all applicable records such as "as built'' drawings, equipment Operating & Maintenance (O&M) manuals, manufacturers spare parts lists and warranty certificates. HCC Facilities and Operations shall retain all O&M manuals, drawings and other relevant data.
13.17. Warranty Administration - the Contractor shall administer and coordinate all warranties provided by construction contractors and equipment suppliers. The Contractor shall perform all work such that all warranties are maintained in full force and effect. The Contractor shall first check the equipment for problems before calling the warranty contractor.
13.18. Employee Turnover
13.18.1. The Contractor must keep an active pool of employee and subcontractor contacts. In the event of resignation of an employee or subcontractor, the Director of FE/M or designee must be notified immediately. An acceptable replacement must be on board by the end of a one-week period. Monthly FTEs list update will be provided to the Director of FE/M.
13.18.2. If a suitable replacement is not replaced within seven (7) days, the Contractor will credit the wages of the terminated employee or subcontractor cost back to HCC until a replacement is identified and accepted by HCC.
13.19. Service Requests - student and employee comfort and satisfaction are of paramount importance. Any student or employee calls requesting service or registering a complaint must be responded to in person and, if possible, resolved within two (2) hours of initial receipt of call. Any second call for services/complaint shall be elevated to the Residence Manager (RM) or General Manager (GM). Failure to satisfy a complaint that has been brought to the attention of the appropriate HCC administrator will be discussed with the Contractor and could be considered failure to meet the requirements of this contract.
13.20. Computerized Maintenance Management System
13.20.1. The Contractor shall develop, implement and maintain effective programs for the standardization of maintenance, utilizing HCC's computerized maintenance management system. All information contained in the computer system and files is the property of HCC.
13.20.2. The Contractor shall establish and maintain the computerized work order system that will serve as a mechanism for other departments requesting work and will serve as a means of instruction of work to be done. The system will, but not limited to, record the cost and completion date or each work order by room, building, campus and college. All work orders shall be distributed, completed and closed out by the Contractor.
13.21. Historical corrective maintenance on equipment shall be documented in the CMMS. All files and related electronic hardcopy information shall be the property of HCC.
13.21.1. CMMS shall be utilized for, but not limited to:
13.21.1.1. Work Order Management
13.21.1.2. Preventive Maintenance Management
13.21.1.3. Labor Management
13.21.1.4. Workflow Management
13.21.1.5. Materials Management
13.21.1.6. Asset and Equipment Management
13.21.1.7. Purchasing and Accounts Payable
13.21.1.8. Automating Work Orders
13.21.1.9. Controlling Parts Inventories
13.21.1.10. Tracking Assets
13.21.1.11. Creating Purchase Orders
13.21.1.12. Easily Accessing Needed Reports
13.21.1.13. Estimate Creation, Routing and Approvals
13.21.1.14. Project Management
13.21.1.15. Assessments for Current Buildings, Components and Assets
13.21.1.16. Deferred Maintenance Identification/tracking
13.21.1.17. Classification of Ratings and Priorities
13.21.1.18. Collection of Cost Estimates
13.21.1.19. FCI Calculations
13.21.2. Training - Awardee shall provide, as needed, on-site training to Houston Community College Facility staff on the functions of the software.
13.21.3. Set-up and Implementation - Awardee shall assume the responsibility for CMMS set up and implementation.
13.21.4. Updates - Proposers shall provide information on software updates with proposals. How often updates are generally provided and any additional costs for the updates.
13.22. Service Desk- campus service center
13.22.1. The Contractor shall provide a service desk to receive all calls including, but not limited to, complaints, and repair and service requests.
13.22.2. The Contractor's dispatcher will create work orders on the CMMS for all calls and forward the work orders to the Maintenance Supervisor at each individual campus for the appropriate response. Priority must be set for each order.
13.23. Clarification of Maintenance Terminology:
13.23.1. Maintenance - The recurring day-to-day, periodic or scheduled work requirement to preserve or restore a facility or equipment to such a condition that it may be effectively utilized for its designated purpose.
13.23.2. Plant Operations - The process of carrying out the necessary procedures, including manual control, attendance and supervision, to affect the performance of the design function of a facility or equipment.
13.24. Requisition Maintenance - Maintenance actions, not part of a normal plan operations and/or maintenance, shall include special construction projects, modernization, alterations and facilities improvements. Director of FE/M or designee must approve all such order in advance. Projects will be subject to the job order contracting process. Documents shall be submitted as a Task of Work (TOW).
13.24.1. Project-external - Certain major repairs and special maintenance maybe performed by other external Contractors. The maintenance contractor shall cooperate fully with HCC and its external contractor(s) in such situations. The successful contractor may be required by HCC to:
13.24.1.1. Assist in planning the desired work.
13.24.1.2. Prepare procurement specifications as desired by HCC.
13.24.1.3. Supervise entirely or assist in the supervisory of the external Contractor(s).
13.24.1.4. Work cooperatively with other external Contractor(s) as directed by HCC Director of FE/M or designee.
13.24.1.5. Coordinate operations activities under its supervision with any projects undertaken by the outside Contractor(s).
13.24.2. Note: There will be no additional cost in the assistance of above requirements by the maintenance engineering service contractor. The cost of HCC Facilities projects to be completed by other external Contractor(s) shall be the responsibility of HCC and shall not be considered part of this contract between HCC and the Contractor hired for Maintenance Engineering Service.
13.25. Repair and Maintenance of Equipment
13.25.1. Repair maintenance include all repair, replacement and adjustment of equipment in response to conditions discovered during performance of preventive maintenance, equipment breakdown/improper operation, or employee complaint. Except in response to employee complaints or safety requirements, repair work orders shall be scheduled for completion depending on priority, availability or parts, workload and convenience of occupants. Priority shall be set as Emergency (All Life Safety), all items that may cause damage to property.
13.25.2. Repair maintenance involving safety considerations or possible damage to property shall be responded to immediately.
13.25.3. Repair maintenance involving the use of a facility shall be responded to immediately.
13.26. Financial and Materials Management
13.26.1. Objectives - The Contractor shall fulfill operations and maintenance management responsibilities with a strong and continued attention to fiscal responsibilities. The objectives of the financial and materials management program are, but not limited to:
13.26.1.1. To strive for increased effectiveness at less costs through improved management and engineering practices.
13.26.1.2. To disseminate written instructions necessary to the fiscal management of operations, maintenance, equipment and supplies.
13.26.1.3. To comply with established fiscal control systems and directives.
13.26.1.4. To budget appropriate cost annually, the Contractor shall prepare plant operations and maintenance financial and statistical data to assist HCC in preparation of its budgets. The Contractor shall monitor expenditures as designated by HCC Facilities in accordance with Texas/Federal law. The Contractor will prepare and submit a monthly detailed expenditure and budget report.
13.26.1.5. To cost allocate, the Contractor will configure the CMMS work order system to properly allocate expenditures to designated cost centers.
13.26.1.6. To purchase appropriate material and equipment in a timely manner to ensure cost savings and competitive bidding as necessary, the Contractor shall provide written policies and instructions based on HCC Facilities requirements governing the purchase of plant operations and maintenance materials, supplies, equipment and utilities.
13.26.1.7. To provide a written tool policy.
13.26.2. Receipt, Storage and Issue of Materials - The Contractor shall provide procedures, in accordance with HCC directives and guidance, necessary to the implementation of programs for the proper inspection, charges, storage, inventory, security and issue of plan operations and maintenance supplies and equipment.
13.26.3. Regulatory Requirement - The Contractor shall implement programs to ensure that HCC Facilities comply with local, state, federal and other regulatory agencies, as they apply, but not limited to, the regulations, codes, inspections, operation and maintenance of the system.
13.26.4. Technical Support - The Contractor shall provide at its own expense professional services and technical resources in support of its field management to:
13.26.4.1. Perform research in determination of HCC Facilities plant operations and maintenance management needs, resources, utilization, programs, procedures and systems.
13.26.4.2. Implement technical support programs for system implementations, training, control inspection and consultant services relating to System plant operations and maintenance management.
13.26.4.3. Consult and make recommendations concerning the plant operations and maintenance aspects of Facility Maintenance service proposals.
13.26.4.4. Provide program to follow progress of major modernization and new construction projects.
13.26.5. Building Alterations
13.26.5.1. The Contractor shall provide consultation for minor rearrangement of HCC spaces, equipment and furniture as needed.
13.26.5.2. The Contractor shall consult Director of FE/M or designee in the planning of major structural alternations, including, but not limited to, supply estimations, etc., as requested by HCC facilities as needed.
13.26.6. Projects – Internal - The Contractor personnel shall supervise minor building alterations in accordance with Designs originated by others and approved by Director of FE/M or designee. The Contractor shall make installations, fabrications, alterations and special projects in accordance with the resources of staff, finances, material, time and space allotted to the plant operations and maintenance organization and as authorized by Director of FE/M.
13.26.6.1. All alteration, modification and addition to buildings, major systems, sub-systems major equipment and ground items of significance shall be approved in advance, in writing by Director of FE/M or designee.
13.26.6.2. Director of FE/M or designee must approve all requisitions requiring the expenditure of funds in advance, in writing and are not included in the Contractor's contract.
13.26.7. Projects – External - Certain major repairs and special maintenance may, be performed by other external contractors. The Contractor shall cooperate fully with HCC and its external Contractor(s) in such situations. The Director of FE/M or designee may contact with the Contractor for such services by utilizing HCC Procurement Operations or job order contracting process. The successful proposer may be required by the System to:
13.26.7.1. Assist in planning the desired work.
13.26.7.2. Prepare procurement specifications as desired by HCC.
13.26.7.3. Supervise entirely or assist in the supervision of the external Contractor(s).
13.26.7.4. Work cooperatively with the other external Contractor(s) as directed by HCC’s Director of FE/M.
13.26.7.5. Coordinate operations activities under its supervision with any projects undertaken by the outside Contractor(s). The cost of HCC facilities projects to be completed by other external Contractor(s) shall be the responsibility of HCC and
13.26.7.6. Shall not be considered part of this contract between HCC and the Contractor hired for facility maintenance services.
13.26.8. Functional Safety and Sanitation
13.26.8.1. The Contractor shall assist in the collection of available documentary evidence of structural safety and building safety compliance (such as Statement of Construction and Fire Protection) as needed for accreditation requirements.
13.26.8.2. The Contractor shall maintain on file documents and certification of the Physical Plant's compliance with the requirement of applicable local, state and federal codes, laws and regulations.
13.26.8.3. The Contractor shall make recommendations to Administration to facilitate compliance with applicable uniform building codes, uniform fire codes, state and/or federal Occupational Health and safety Codes, and Life Safety Codes.
13.26.8.4. The Contractor shall maintain good safety practices within the maintenance facility areas and keep equipment, spaces and shops in a tidy condition and participate in the System's safety programs.
13.26.9. Quality Assurance / Quality Control of Service - The following quality performance review will be initiated to insure a high standard of service for the College:
13.26.9.1. The Contractor’s RM/GM will make weekly inspections. The Contractor and Director of FE/M or designee will make bi-weekly inspections. Deficiencies must be corrected prior to the next regular session.
13.26.9.2. Daily activities shall be maintained in the CMMS and be available for review by HCC within 24-hours. Preventive maintenance schedules with notation of performance shall be maintained for management control, inspection and HCCs review.
13.26.9.3. Corrective maintenance requisition actions shall be tabulated by category and included in the monthly report.
13.26.9.4. Monthly summary of plant operations and maintenance functions, accomplishments and objectives shall be prepared and presented for comments, additions and concurrence of HCC Facilities and included in the monthly report.
13.26.9.5. The Contractor shall meet as requested with the contract administrator to discuss the contract.
13.26.9.6. The Contractor's manager must carry portable communications equipment for communication with Director of FE/M or designee and other designees. There will be a 24-hour a day cell phone available to reach the Contract manager and RM.
13.26.9.7. A Contractor's employee satisfaction measure will be designed. HCC shall receive a report of the employee satisfaction yearly. This report will also include all training and licenses accomplished or received for the past year.
13.26.10. Environmental Laws
13.26.10.1. Contractor shall comply with all rules, regulations, statutes or orders of, but not limited to, the Environmental Protection Agency ("EPA"), the Texas Commission on Environmental Quality (''TCEQ"), and any other local, state or federal governmental agency with the authority to promulgate environmental laws and regulations.
13.26.10.2. Contractor shall promptly reimburse Houston Community College (HCC) for any fines or penalties levied against the City because of the Contractor's failure to comply.
13.26.10.3. Contractors and their employees who used chemicals during the performance of their jobs must have completed Hazard Communication training in compliance with the Texas Hazard Communication Act. The Texas Health and Safety Code.
13.26.10.4. Contractors must supply HCC with a copy of the Safety Data Sheet (SDS) for all chemicals brought onto HCC properties and must dispose of all chemicals supplied by the Contractor after use at the Contractor's expense.
13.26.11. Hazardous Materials
13.26.11.1. The Contractor shall not possess, use, generate, release, discharge, store, dispose of or transport any Hazardous Materials on, under, in, above, to, or from the site except in strict compliance with any and all local, state and federal environmental laws or regulations.
13.26.11.2. In the event of Hazardous Materials generated by the Contractor or Subcontractor, the Contractor or Subcontractor is responsible to pay for the proper disposal of Hazardous Materials. "Hazardous Materials" means any substances, materials, or wastes that are or become regulated as hazardous or toxic substances under any applicable federal, state, or local laws, regulations, ordinances or orders.
13.26.11.3. The Contractor shall not deposit paint, oil, gasoline, grease, lubricants or any ignitable or hazardous liquids, materials, or substances in the City's storm sewer system or sanitary sewer system or elsewhere on HCC property in violation of any local, state or federal environmental laws or regulations.
13.26.11.4. It is the responsibility of the Contractor and Subcontractor to remove any materials, solvents, or substances from HCC after a maintenance project is complete.
13.26.12. Maintenance Audit
13.26.12.1. The Chief Facilities Officer or designee may conduct a maintenance audit, either alone or accompanied by the Contractor, or may request that the Contractor conduct a maintenance audit, or may select a qualified third party to perform a maintenance audit. Such an audit shall include, but not limited to, inspection of the premises, equipment, inventory, records, logs, and work performance at each facility. The audit shall be conducted without prior notice to the Contractor. The audit results shall be provided to the Contractor.
13.26.12.2. The Contractor shall correct any discrepancies identified and covered under the terms of this agreement within five (5) working days after the audit results are provided to the Contractor.
13.26.12.3. The Contractor shall provide Director of FE/M or designee a written explanation for each discrepancy and corrective action taken within ten (10) days after the audit results are provided to the Contractor. Further, the contractor shall provide the Director of FE/M with an inspection and maintenance plan to prevent future occurrences of any problems identified in the audit. The Director of FE/M may use the results of the audit to terminate this Agreement, regardless of any corrective action taken by the Contractor.
14. EXCLUSIONS
14.1. Fire system component repair due to renovation, code changes, or current yellow. Contractor has the burden to prove this condition
14.2. Building Operations such as unlocking of doors, events preparation, furniture and educational materials moving, and all other tasks not directly related to facilities maintenance
14.3. Door locking hardware, latches pad locks
14.4. Structural repair and associated damages
14.5. Cafeteria and food service equipment repair and/or maintenance tasks
14.6. Repair/Replacement of items or equipment damaged by vandalism, acts of God, or other circumstances that result in failure that is beyond Contractor's control
14.7. Classroom equipment for teaching purposes
14.8. Replacement of obsolete equipment
14.9. Permit fees, fines and other costs associated with regulatory compliance that is not under the Contractor's control
14.10. Furniture repair
14.11. General maintenance
14.11.1. Paint
14.11.2. Wall repair
14.11.3. Ceiling tile replacement
14.11.4. Carpet repair
14.11.5. Finish material maintenance
14.11.6. Manual doors/hardware
14.11.7. Tile repair
14.11.8. Parking lot repair
14.11.9. Wheel stop maintenance
14.11.10. Window repair
14.11.11. Roofing maintenance
14.12. Above and attached is an overview of the full comprehensive requirements of the required responsibilities and duties of the contractor. This contract is intended to be full maintenance services for the Houston Community College System to maintain and operate the equipment within the HCC portfolio in an effective and efficient manner and so there shall be no disruption of normal day to day activities of the college. Other than exclusions, the contractor is responsible for all building components and systems necessary to operate a facility functionally and safely within all guidelines of city, state, and federal code to APPA standard three (3) guidelines. This includes the mechanical functionality of the overall portfolio and associated components of listed facilities.